# Active Construction - Progress Inspections

## Golden Row Inspection

|  | Golden Row Inspection |  |
| --- | --- | --- |
| DESCRIPTION | The Golden Row Inspection is performed early on in project construction to witness, and potentially correct, installation means and methods before the site is fully constructed. In this phase, typically 100% of the installed components may be inspected. If the installation has progressed significantly beyond the first few rows of PV modules, then a standard sampling approach will be employed. See the detailed scope below. |  |
| BEST FOR | This inspection level is appropriate to evaluate construction safety, quality, and operational risks before the system is fully constructed. |  |
| RESOURCES | Team of 1 Engineers for up to 1 day* |  |
| REPORTING | 5 days from the inspection |  |
| DETAILED SCOPE OF WORK |  | Golden Row Inspection |
| Documentation review |  | Full set |
| Engineering drawings |  | Full set |
| Visual Inspection (components installed so far): |  |  |
| - General roof/site condition |  | 100% |
| - Interconnection and metering |  | 100% |
| - AC terminations (PV, BESS, GenSet, and EV Charging where applicable) |  | 100% |
| - AC distribution system (PV, BESS, GenSet, and EV Charging where applicable) |  | 100% |
| - AC protections: AC disconnects and AC breakers (PV, BESS, GenSet, and EV Charging where applicable) |  | 100% |
| - PV Inverters (string or central) |  | 100% Central / Sample ISO 2859 String |
| - DC distribution system (PV) |  | Sample ISO 2859 |
| - PV racking attachment points to the roof or ground |  | Sample ISO 2859 |
| - PV racking attachments and bonding to the PV modules |  | Sample ISO 2859 |
| - PV module wire management |  | Sample ISO 2859 |
| - RSDs installation and wire management |  | Sample ISO 2859 |
| - Wire management of transitions from PV modules, RSDs, racking, conduit, cable trays, combiner boxes, and terminations. |  | Sample ISO 2859 |
| - Wire terminations in combiner boxes, PV inverters, and AC panels. |  | Sample ISO 2859 |
| - PV connector making process, associated tools, and procedures along with installation of connectors. |  | Sample ISO 2859 |
| - Conduits / Cable trays |  | Sample ISO 2859 |
| - Combiner Boxes |  | Sample ISO 2859 |
| - Rapid Shutdowns Devices (“RSDs”) (when applicable) |  | Sample ISO 2859 |
| - Field-made connectors |  | Sample ISO 2859 |
| - Factory-made connectors |  | Sample ISO 2859 |
| - PV Modules |  | Sample ISO 2859 |
| List of Nonconformities |  | Included |

## Pre-Commissioning Inspection / Mechanical Completion Inspection / Cold

|  | Pre-Commissioning Inspection |
| --- | --- |
| DESCRIPTION | The Pre-Commissioning Inspection aims to evaluate the quality of construction and workmanship for the projects. This scope consists of an engineering design review plus a comprehensive visual inspection. HelioVolta uses a detailed checklist with 300+ points combined with a statistically significant sampling approach based on ISO 2859-1 to maximize findings and minimize risk. |
| BEST FOR | This inspection is best for projects that have achieved mechanical completion and are preparing to start operations. Focused on addressing quality-related items that would need to be addressed as part of the EPC punch list. Can be used as an independent “special inspection” in jurisdictions requiring it prior to permit signoff. |
| RESOURCES | Team of 1-2 Engineers for up to 1 day* |
| REPORTING | 5 days from the inspection |

| DETAILED SCOPE OF WORK | Post-Commissioning INSPECTION |
| --- | --- |
| Documentation review | Full set |
| Engineering drawings as-built review | Full set |
| System design and specifications match construction drawings | Verification |
| Commissioning documentation and testing results review | Full set |
| Data Acquisition System (DAS) installation and communication | Inspection and Verification |
| Visual Inspection: Safety hazards, damage, bad practices, workmanship, code compliance, improper installation, abnormal conditions, misalignments, corrosion, labels, torque, improper operation, breakages, loose connections, water/moisture intrusion, positioning, bonding, grounding… |  |
| - General site condition | 100% |
| - Interconnection and metering | 100% |
| - AC protections: AC disconnects and AC breakers | 100% |
| - Inverters (central, microinverter or string) | 100% Central / Sample ISO 2859 others |
| - Rapid shut down, optimizers, and other MLPE | Sample ISO 2859 |
| - DC Distribution system and wire management | Sample ISO 2859 |
| - Combiner Boxes (when applicable) | Sample ISO 2859 |
| - Field-made connectors | Sample ISO 2859 |
| - Factory-made connectors | Sample ISO 2859 |
| - PV Modules | Sample ISO 2859 |
| IV-Curve tracing – per string | Optional |
| ISC – VOC measurements – per string | Optional |
| Insulation resistance test – per string | Optional |
| Continuity testing | Optional |
| Punch list generation | Included |

## Post-Commissioning / Substantial Completion Inspection / Hot

|  | Post Commissioning Inspection |
| --- | --- |
| DESCRIPTION | The Post-Commissioning Inspection aims to evaluate the quality of construction and workmanship for the projects. This scope consists of an engineering design review plus comprehensive visual and thermal inspection. HelioVolta uses a detailed checklist with 300+ points combined with a statistically significant sampling approach based on ISO 2859-1 to maximize findings and minimize risk. |
| BEST FOR | This inspection is best for projects that have achieved substantial completion or final commissioning and are starting operations. Focused on addressing quality-related items that would need to be addressed as part of the EPC punch list. |
| RESOURCES | Team of 1-2 Engineers for up to 1 day* |
| REPORTING | 5 days from the inspection |

| DETAILED SCOPE OF WORK | Post-Commissioning INSPECTION |
| --- | --- |
| Documentation review | Full set |
| Engineering drawings as-built review | Full set |
| System design and specifications match construction drawings | Verification |
| Commissioning documentation and testing results review | Full set |
| Data Acquisition System (DAS) installation and communication | Inspection and Verification |
| Visual Inspection: Safety hazards, damage, bad practices, workmanship, code compliance, improper installation, abnormal conditions, misalignments, corrosion, labels, torque, improper operation, breakages, loose connections, water/moisture intrusion, positioning, bonding, grounding… |  |
| - General site condition | 100% |
| - Interconnection and metering | 100% |
| - AC protections: AC disconnects and AC breakers | 100% |
| - Inverters (central, microinverter or string) | 100% Central / Sample ISO 2859 others |
| - Rapid shut down, optimizers, and other MLPE | Sample ISO 2859 |
| - DC Distribution system and wire management | Sample ISO 2859 |
| - Combiner Boxes (when applicable) | Sample ISO 2859 |
| - Field-made connectors | Sample ISO 2859 |
| - Factory-made connectors | Sample ISO 2859 |
| - PV Modules | Sample ISO 2859 |
| Thermal imaging: Hot connections, outside temperature range, hot spots, temperature deltas, excessive temperatures… |  |
| - AC protections and AC breakers, terminations | 100% |
| - Inverters (central, microinverter or string) | 100% Central / Sample ISO 2859 others |
| - Rapid shut down, optimizers, and other MLPE | Sample ISO 2859 |
| - DC Distribution system, splices, junction boxes, and terminations | Sample ISO 2859 |
| - Combiner Boxes, terminations | Sample ISO 2859 |
| - Field-made connectors | Sample ISO 2859 |
| - Factory-made connectors | Sample ISO 2859 |
| - PV Modules | Sample ISO 2859 |
| IV-Curve tracing – per string | Review commissioning data |
| ISC – VOC measurements – per string | Review commissioning data |
| Insulation resistance test – per string | Review commissioning data |
| Continuity testing | Optional |
| Punch list generation | Included |

## Final Walk Inspection

|  | Final Walk Inspection |
| --- | --- |
| DESCRIPTION | The Final Walk Inspection aims to verify the remediation of issues generated from the punch list on the Post-Commissioning Inspection. This scope consists of a comprehensive visual and thermal inspection (including 100% of modules) if not already completed. HelioVolta will verify and document issues in SolarGrade and provide reports for use in regular O&M maintenance. |
| BEST FOR | This inspection is best for larger projects or higher profile projects. Focused on addressing and verifying quality-related items that would impact operations. |
| RESOURCES | Team of 1-2 Engineers for up to 1 day* |
| REPORTING | 5 days from the inspection |

# Active Asset – Assessments / Testing

## Health Assessment Inspection (Hot)

|  | HEALTH ASSESSMENT INSPECTION |
| --- | --- |
| DESCRIPTION | The health assessment inspection aims to identify safety and quality-related risks of operational systems. This scope consists of an engineering design review, comprehensive visual and thermal inspection. HelioVolta uses a detailed checklist with 300+ points combined with a statistically significant sampling approach - ISO 2859- to maximize findings and minimize risk. |
| BEST FOR | This inspection is best for technical audits to assess the overall health condition. Mostly focused on safety, quality, and reliability. |
| REPORTING | 5 days from the inspection |

| DETAILED SCOPE OF WORK | HEALTH ASSESSMENT INSPECTION |
| --- | --- |
| Documentation review | Full set |
| Engineering drawings review | Full set |
| O&M Logs | Included |
| Visual Inspection: Safety hazards, damage, bad practices, workmanship, code compliance, improper installation, abnormal conditions, misalignments, corrosion, labels, torque, improper operation, breakages, loose connections, water/moisture intrusion, positioning, bonding, grounding… |  |
| - General site condition | 100% |
| - Interconnection and metering | 100% |
| - AC protections: AC disconnects and AC breakers | 100% |
| - Inverters (central, microinverters or string) | Sample ISO 2859 |
| - Rapid shut down, optimizers and other MLPE | Sample ISO 2859 |
| - DC Distribution system and wire management | Sample ISO 2859 |
| - Combiner Boxes | Sample ISO 2859 |
| - Field-made connectors | Sample ISO 2859 |
| - Factory-made connectors | Sample ISO 2859 |
| - Modules | Sample ISO 2859 |
| Thermal imaging: Hot connections, outside temperature range, hot spots, temperature deltas, excessive temperatures… |  |
| - AC protections and AC breakers, terminations | Sample ISO 2859 |
| - Inverters (central, string or microinverters) | Sample ISO 2859 |
| - DC Distribution system, splices, junction boxes and terminations | Sample ISO 2859 |
| - Rapid shut down, optimizers and other MLPE | Sample ISO 2859 |
| - Combiner Boxes, terminations | Sample ISO 2859 |
| - Field-made connectors | Sample ISO 2859 |
| - Factory-made connectors | Sample ISO 2859 |
| - Modules | Sample ISO 2859 |
| IV-Curve tracing | Not included |
| ISC – VOC measurements | Not included |
| Insulation resistance test | Not included |
| Continuity testing | Not included |
| Punch list generation | Included |

## TDD Assessment Inspection – Light (work needed)

|  | Assessment Inspection |
| --- | --- |
| DESCRIPTION | The TDD Light Assessment Inspection aims to find safety and quality-related risks of an operational site. This scope consists of a visual inspection focusing on the following areas. - Overall site condition - Installation matches drawings, including major equipment selection - Installation is compliant with code and industry best-practices - Identification of critical issues / fatal flaws This inspection may not include operating the system, opening equipment enclosures, or thermal imaging, depending on the operational status and what support resources are available on site. |
| BEST FOR | This inspection is best for technical audits to assess the overall health condition with a focus on safety, reliability, and critical risk identification. |
| RESOURCES |  |
| REPORTING |  |

## Inspection and Operational Qualification (work needed)

|  | Inspection and Operational Qualification |
| --- | --- |
| DESCRIPTION |  |
| BEST FOR |  |
| RESOURCES |  |
| REPORTING |  |

| Inspection and Operational Qualification (IOQ) Task | Quantity to inspect |
| --- | --- |
| Engineering drawings as-built | Full set |
| Communication system review and validation (DAS) | Verification |
| Visual Inspection: |  |
| - General roof condition | 100% |
| - Interconnection and metering | 100% |
| - AC Distribution system | 100% |
| - AC protections: AC disconnects and AC breakers | 100% |
| - Inverters | 100% |
| - DC Distribution system | Sample ISO 2859 |
| - Conduits | 100% |
| - Cable Trays | 100% |
| - Combiner Boxes | 100% |
| - Module Level Electronics | Sample ISO 2859 |
| - Field made connectors | 100% |
| - Factory-made connectors | Min. 20% |
| - Modules1 | Dynamic Sampling |
| Thermal imaging: |  |
| - AC protections: AC disconnects and AC breakers | 100% |
| - Inverters (string) | 100% |
| - DC Distribution system | Sample ISO 2859 |
| - Junction Boxes and other enclosures | 100% |
| - Combiner Boxes | 100% |
| - Field made connectors | 100% |
| - Factory-made connectors | Min 20% |
| - Modules | 100% |
| IV-Curve tracing2 (if applicable) | Sample ISO 2859 |
| Insulation resistance test3 (IRT) | Review IRT Commissioning documentation |
| - AC wiring-subject to installed equipment |  |
| - DC wiring-upon request and subject to installed equipment. |  |
| Continuity testing | Sample ISO 2859 |

## RCA Phase 1 – Technical Investigation

|  | Technical Investigation |
| --- | --- |
| DESCRIPTION | The Technical Investigation Inspection aims to determine the root cause of the failures on-site and identify safety, reliability, performance, and quality-related risks of the project. This scope consists of a comprehensive visual and thermal inspection, as applicable. HelioVolta uses a statistically significant sampling approach, ISO 2859, to maximize findings and minimize risk. Specifically, the inspection will focus on the following: - On-site visual inspection to observe as-built conditions and verify major equipment installation practices, including: - Wire management of DC combiner harnesses - DC distribution cabling - Tracker operation and effects on DC distribution - Collect additional data on failure modes of Shoals T-joints - Determination of scope and sample for further testing methods. - Author a report detailing the work performed and assessment of the failures. |
| BEST FOR | This inspection is best for root cause analyses with a focus on root cause determination, safety, and reliability. |
| RESOURCES | Team of 2 Engineers for 2-3 days |
| REPORTING | 10 days from the inspection |

## XCT Connector Testing

|  | XCT Connector Testing |
| --- | --- |
| DESCRIPTION | X-ray Computed Tomography (XCT) Connector Testing involves imaging connector specimens in a lab setting using advanced X-ray methods. The testing gives a clear picture of how a connector was installed, its associated workmanship, and component deficiencies. Typical findings include analysis of the crimps and conductor strands, confirmation of proper back nut threading, confirmation of gland seal around insulation, proper seating of male and female contacts, and verification of structural integrity. Testing on the connector specimens is non-destructive, though the specimen must be removed from site, and it would be impractical to reinstall after testing. HelioVolta provides analysis of the test data collected as the labs doing this work rarely have domain expertise in solar components. The sample size per site will be 5 male-female connector pairs from the home run conductor. HelioVolta typically uses ISO 2859 to determine a statistically significant sampling size for this testing. |
| BEST FOR | This testing is best for in-depth technical assessment of connector specimens as teams pursue safety and reliability |
| RESOURCES | The connector samples must be collected per typical evidence collection protocols. Client will collect these samples and deliver to HelioVolta’s designated lab. Alternatively, these may be gathered by the HelioVolta team during another scope of work engagement. Else, a third party may also be used to collect specimens. HelioVolta works with a lab partner to perform the XCT scanning. |
| REPORTING | 10 days after HelioVolta receives data from the test lab. |

## Aerial Thermal Inspection

|  | Aerial thermal Inspection |
| --- | --- |
| DESCRIPTION | The Aerial Thermal Inspection will be carried out to identify defects or anomalies in the PV system that could potentially impact its performance and reliability. Drone infrared imagery will include: - A pre-inspection meeting to discuss and establish the necessary safety protocols and procedures. - Aerial inspection using a drone equipped with a thermal camera. The drone will be flown over the solar modules, capturing thermal images. - Analysis of thermal images to identify anomalies or defects in the system. - A report will be prepared detailing the findings of the inspection. |
| BEST FOR | This inspection is best for larger projects. Focused on exposing electrical concerns that may be missed through a normal visual inspection. |
| RESOURCES | Team of 1-2 Engineers for up to a day* |
| REPORTING | 5 days from the inspection |